## Slide 1: Learning Based Compact Thermal Modeling for Energy-Efficient Smart Building Management
Hengyang Zhao, Daniel Quach,
Shujuan Wang, Hai Wang,
Hai-Bao Chen, Xin Li,
Sheldon, X.-D. Tan
Department of Electrical Engineering
University of California, Riverside, CA

## Slide 2: Outline
Motivation
Review of EnergyPlus program
Review of RNN architectures
RNN-based thermal modeling methods
  Two RNN implementations
  Cross validation for accuracy improvement
Experimental results
Summary

## Slide 3: Motivation
Building section accounts for about 40% energy consumption in United States
Building section is also responsible for 70% of electricity use
About 50% of the energy consumed in buildings are directly related to space heating, cooling and ventilation (HVAC) [1]
For energy-efficient smart building, efficient HVAC control is required. Hence, compact yet accurate building thermal modeling is required
Chart: 

## Slide 4: EnergyPlus Software
A fully integrated building, envelope, HVAC, water, and renewables simulation program
Originally based on BLAST and DOE-2.1E
Has rich GUI-based tools/plugins as front-end such as Google SketchUp.
Calculations are based on first-principle based numerical methods
  High computational costs
  Not suitable for control-based analysys
Needs detailed structures or equations of the thermal systems

## Slide 5: HVAC System

## Slide 6: Some building cases from EnergyPlus
2-zone data center
5-zone office building
6-zone office building

## Slide 7: EnergyPlus Simulation
INPUTS: Ambient temperature, people factors, equipment factors, HVAC inputs, etc.
OUTPUTS: Temperatures of the interested spaces/rooms
Ambient Temperature
Light Heating Rate
Electrical Equipment Heating Rate
Ambient Temperature
Air System Cooling Rate (Zones)
Air System Cooling Rate (Plenum)

## Slide 8: Non-linear control
Advanced control method is needed in order to minimize HVAC energy cost and meet the temperature goal
  EKF: Extended Kalman Filter [2]
  Computational cost is sensitive to number of state variables
We need a compact thermal model to describe the smart building system, with acceptable modeling error

## Slide 9: NLSS architecture
NLSS: Non-linear State Space neural network [3]
  Closer to non-linear state space representation
  Slightly higher variance in experiment

## Slide 10: ELNN architecture
ELNN: Elman’s Neural Network [4] with local feedbacks
  More works to extract the state variables (since they are everywhere with each layer)
  Slightly lower variance in experiment

## Slide 11: RNN for thermal model of building
Programmed in Python, with libraries PyBrain [5], NumPy [6], SciPy [7], Matplotlib [8]
2-norm regularization enabled in training to mitigate the over-fitting problem
We use RPropMinus [9], an adaptive back-propagation algorithm to train the RNNs
Input data is normalized before fed into the trainer to speed up training
Baseline data configuration:
  Months 1-3, 5-7, 9-11 for training, 4, 8, 12 for validation

## Slide 12: Network configurations
Empirical number of layers:
  2 hidden layers for ELNN, 4 hidden layers for NLSS
Empirical size of layers:
  ELNN
    Hidden layer #1:
    Hidden layer #2:
  NLSS
    Hidden layer #1-3:
    Hidden layer #4:
    Example: NLSS in 2-zone (all factors, #IN=11, #OUT=2): Uses layers with size (20, 20, 20, 2)

## Slide 13: Error calculation
On each sampled output, we use two methods to calculate the modeling error
  Absolute error: the actual difference between RNN output and EnergyPlus output:
  Relative error: Absolute error divided by EnergyPlus output:
Average and maximum statistics are also calculated over the whole training data and validation data respectively

## Slide 14: 6-fold cross validation
We use every adjacent 2 months as a group
In each run of cross validation, we use one group to validate the model trained by the rest 5 groups
In 6-zone building RNNs
  Validation error reduced from 34% to 23% in NLSS; from 23% to 16% in ELNN

## Slide 15: 2-zone (all factors) modeling result
#IN=11, #OUT=2
Average error
  ELNN 0.022°C/0.10%; NLSS 0.026°C/0.11%
Maximum error
  ELNN 0.24°C/1.1%; NLSS 0.21°C/0.94%

## Slide 16: 2-zone (HVAC) modeling result
#IN=3, #OUT=2
Average error
  ELNN 0.20°C/0.98%; NLSS 0.23°C/1.2%
Maximum error
  ELNN 1.34°C/6.5%; NLSS 1.4°C/7.0%

## Slide 17: 5-zone (all factors) modeling result
#IN=26, #OUT=5
Average error
  ELNN 0.23°C/1.0%; NLSS 0.31°C/1.4%
Maximum error
  ELNN 4.4°C/16%; NLSS 4.6°C/20%

## Slide 18: 5-zone (HVAC) modeling result
#IN=6, #OUT=5
Average error
  ELNN 0.16°C/0.71%; NLSS 0.057°C/0.26%
Maximum error
  ELNN 2.2°C/12%; NLSS 2.2°C/9.6%

## Slide 19: 6-zone modeling result
#IN=55, #OUT=6
Average error
  ELNN 0.53°C/2.2%; NLSS 0.48°C/2.2%
Maximum error
  ELNN 4.1°C/16%; NLSS 4.8°C/23%

## Slide 20: Summary
We did experiments on two RNN architectures on building thermal models
  ELNN: Elman’s Neural Network with local feedbacks
  NLSS: Non-Linear State Space Neural Network
We used cross-validation to reduce the modeling error on the 6-zone building case
Modeling errors
  Simple 2-zone model: 1% ~ 1.5% relative error
  Bigger 6-zone model: ELNN 16% and Elman 23%

## Slide 21: Thank you!
Reference
  [1] Building Energy Data Book of DOE. [Online]. http: //buildingsdatabook.eren.doe.gov
  [2] M. Massoumy, Q. Zhu, C. Li, F. Meggers, and A. Sangiovanni-Vincentelli, “Co-design of Control Algorithm and Embedded Platform for Building HVAC Systems,” in International Conference on Cyber Physical Systems (ICCPS), Philadephia, PA, Apr. 2013, pp. 61–70.
  [3] S. Haykin and N. Network, “A comprehensive fundation,” Neural Networks, vol. 2, no. 2004, 2004.
  [4] J. L. Elman, “Finding structure in time,” Cognitive science, vol. 14, no. 2, pp. 179–211, 1990.
  [5] T. Schaul, J. Bayer, D. Wierstra, Y. Sun, M. Felder, F. Sehnke, T. Ru ̈ckstieß, and J. Schmidhuber, “PyBrain,” Journal of Machine Learning Research, vol. 11, pp. 743–746, 2010.
  [6] S. Van Der Walt, S. C. Colbert, and G. Varoquaux, “The numpy array: a structure for efficient numerical computation,” Computing in Science & Engineering, vol. 13, no. 2, pp. 22–30, 2011.
  [7] E. Jones, T. Oliphant, P. Peterson et al., “SciPy: Open source scientific tools for Python,” 2001–, [Online; accessed 2015-07-23]. [Online]. Available: http://www.scipy.org/
  [8] J. D. Hunter, “Matplotlib: A 2d graphics environment,” Computing in science and engineering, vol. 9, no. 3, pp. 90–95, 2007.
  [9] C. Igel and M. Hu ̈sken, “Empirical evaluation of the improved rprop learning algorithms,” Neurocomputing, vol. 50, pp. 105–123, 2003.