## Slide 1: Building Thermal Modeling for Energy-Efficient Smart Building Control
Daniel Quach, Shujuan Wang, Jian Ma, Hengyang Zhao, Hai Wang, Sheldon X.-D. Tan
Department of Electrical and Computer Engineering
University of California, Riverside, CA

## Slide 2: Outline
Motivation
EnergyPlus Review
Subspace Identification based method
Initial Results with no extra factors
Results with extra factors
Optimization and Final Results
Summary

## Slide 3: Motivation
Estimated building section makes up about 40% energy consumption in U.S.
Responsible for 70% of electricity use on average households
About 50% of energy consumed in buildings are related to space heating, cooling, and ventilation
Notes: Need to control the heating, ventilation and air conditioning in a more energy-efficient way.

## Slide 4: EnergyPlus
Software package by U.S. Dept. of Energy used for modeling thermal behavior, energy, and water use.
Capable of modifying specific settings for each zone
  Thermal zones, Space type, Schedule, Outdoor Air, People, Lights, Electric Equipment, Surfaces, etc.

## Slide 5: Setting For Each Thermal Zone

## Slide 6: EnergyPlus Results
Use this to get more results

## Slide 7: EnergyPlus Results

## Slide 8: Proposed Method
Implemented using MATLAB with System Identification Toolbox
Used EnergyPlus to simulate model and generate inputs and ‘golden’ outputs
Inputs:
  Ambient temperature, HVAC data, light, electrical equipment, people
Output:
  Zone room temperature

## Slide 9: Initial Results (no extra factors)
Order for system identification: 50
Legend:
  Blue lines are EnergyPlus results
  Red lines are our estimated results
Note: see results between 400 and 500. There is some extra effect that causes the golden result to be strange. Our system does not handle it well for both training (testing) and validation phases.

## Slide 10: Initial Results (Training Phase)

## Slide 11: Initial Results (Validation Phase)

## Slide 12: Results with extra factors
Specifications
  Input:
    Ambient temperature, Custom scheduler, Light Heating Rate
  Output:
    Zone room temperatures
  Order for system identification: 90
Legend:
  Blue lines are EnergyPlus results
  Red lines are our estimated results

## Slide 13: Results (Training Phase)

## Slide 14: Results (Validation Phase)

## Slide 15: Analysis
Testing phase seems to build the model accurately, even with light heat as a factor.
Example below:
Actual schedule(blue) : 4-2-5-2-5-1-4-2-5-2-5-2-…
Estimated schedule(red) : 2-2-5-2-5-2-5-2-5-2-5-2-…
(Underlined numbers are weekend days)

## Slide 16: Model order selection to avoid overfitting
Done various optimization which includes selecting a proper order.
For this order study, the best order seen below is 37. After many trials, we found an acceptable order.

## Slide 17: Final Results (Training Phase)
For 5-zone building, only one zone and the first 500 hours shown below

## Slide 18: Final Results (Validation Phase)

## Slide 19: Absolute and Relative Errors
Five zone with HVAC only considering ambient temperature |  |  |  |  |  | 
 |  | SPACE 1 | SPACE 2 | SPACE 3 | SPACE 4 | SPACE 5
Testing | Relative RMS Error | 0.0150 | 0.0165 | 0.0138 | 0.0136 | 0.0120
 | Max Relative Error | 0.0879 | 0.0825 | 0.0958 | 0.0927 | 0.0900
 | Absolute RMS Error | 0.3078 | 0.3372 | 0.2752 | 0.2739 | 0.2482
 | Max Absolute Error | 1.8780 | 1.7701 | 2.0544 | 1.9978 | 1.9546
Validation | Relative RMS Error | 0.0267 | 0.0290 | 0.0187 | 0.0199 | 0.0166
 | Max Relative Error | 0.1510 | 0.1868 | 0.1438 | 0.1463 | 0.1375
 | Absolute RMS Error | 0.5707 | 0.6267 | 0.3874 | 0.4157 | 0.3538
 | Max Absolute Error | 2.7525 | 4.1471 | 3.2361 | 3.3607 | 3.1209
Five zone with HVAC and considering extra factors |  |  |  |  |  | 
 |  | SPACE 1 | SPACE 2 | SPACE 3 | SPACE 4 | SPACE 5
Testing | Relative RMS Error | 0.0153 | 0.0167 | 0.0132 | 0.0139 | 0.0088
 | Max Relative Error | 0.0792 | 0.0948 | 0.0759 | 0.0788 | 0.0598
 | Absolute RMS Error | 0.3297 | 0.3620 | 0.2742 | 0.2919 | 0.1900
 | Max Absolute Error | 1.7938 | 2.0272 | 1.6310 | 1.6794 | 1.3117
Validation | Relative RMS Error | 0.0320 | 0.0333 | 0.0187 | 0.0203 | 0.0145
 | Max Relative Error | 0.1594 | 0.1690 | 0.0786 | 0.0930 | 0.0650
 | Absolute RMS Error | 0.7247 | 0.7520 | 0.3947 | 0.4352 | 0.3187
 | Max Absolute Error | 4.3228 | 4.6669 | 1.6876 | 2.0009 | 1.4297

## Slide 20: 2-Zone Results
For 2-zone, only one zone and first 500 hours are shown below
Two zone with HVAC and extra factors |  |  | 
 |  | SPACE 1 | SPACE 2
Testing | Relative RMS Error | 0.0021 | 0.0022
 | Max Relative Error | 0.0128 | 0.0144
 | Absolute RMS Error | 0.0476 | 0.0488
 | Max Absolute Error | 0.2959 | 0.3235
Validation | Relative RMS Error | 0.0041 | 0.0060
 | Max Relative Error | 0.0214 | 0.0229
 | Absolute RMS Error | 0.0939 | 0.1338
 | Max Absolute Error | 0.4912 | 0.5164

## Slide 21: Summary
Based on recently proposed subspace identification method
5-zone (all factors)
  1.4 - 3.3% average relative error
  6.5 – 16.9% max relative error
5-zone (HVAC only)
  1.7 – 2.9% average relative error
  13.8 – 18.7% max relative error
2-zone (all factors)
  0.4 – 0.6% average relative error
  2.1 – 2.3% max relative error

## Slide 22
Questions???