## Slide 1: Building Thermal Modeling for Energy-Efficient Smart Building Control
Daniel Quach, Shujuan Wang, Jian Ma, Hengyang Zhao, Hai Wang, Sheldon X.-D. Tan
Department of Electrical and Computer Engineering
University of California, Riverside, CA

## Slide 2: Outline
Motivation
EnergyPlus Review
Subspace Identification based method
Two-stage Modeling
Model order selection
5-zone and 2-zone Results
Summary

## Slide 3: Motivation
Estimated building section makes up about 40% energy consumption in U.S.
Responsible for 70% of electricity use on average households
About 50% of energy consumed in buildings are related to space heating, cooling, and ventilation
Notes: Need to control the heating, ventilation and air conditioning in a more energy-efficient way.

## Slide 4: EnergyPlus
Software package by U.S. Dept. of Energy used for modeling thermal behavior, energy, and water use.
Capable of modifying specific settings for each zone
  Thermal zones, Space type, Schedule, Outdoor Air, People, Lights, Electric Equipment, Surfaces, etc.

## Slide 5: Proposed thermal modeling method
Applied subspace system identification (SID) method to build the dynamic linear thermal model
  Used EnergyPlus to simulate model and generate inputs and ‘golden’ outputs
  Inputs:
    Ambient temperature, HVAC data, light, electrical equipment, people
  Output:
    Zone room temperature

## Slide 6: Behavioral thermal modeling problem
Described as a discrete linear time invariant (LTI) system
p0
p1
p2
p3
p4
t0
t1
t2
t3
t4
A: stable matrix u: input matrix
y: output matrix x: state matrix

## Slide 7: Subspace System Identification[1]
State space models (LTI)
  Here input u is Power, and output y is Temperature
Goal
  Given input and output observations u and y, find an appropriate order n and the system matrices {A, Bu, C}
A : stable matrix w,v : stationary zero-mean white-noise seq.
u/y : input/output
[1] N.Y. Chen, J.S. Gibson, “Subspace System Identification Using a Multichannel Lattice Filter”, Proc. American Control Conference, 2004, Volume 1, Issue 30, pp. 855 - 860
Considering
Noise!
Notes: A is a stable matrix. The sequences w, and v are stationary zero-mean white noise sequences. Only the
sequences y and U are measured. Our goal is to use the measured y and U to identify unbiased system matrices
(A, B", C).
recursive least-squares (RLS) estimation.

## Slide 8: SID algorithm flow see [1] for more details
QR
Input/Ouput Data
u(t), y(t)
Weighted
Hankel Matrix
HRT
SVD
HRT=UΣVT
Extended Observability
/Controllability Matrix
O(M)=UrΣr1/2
C(N)= Σr1/2VrT(RT)-1
Reduced SVD
HRT=UrΣrVrT
C = first top block row of O(M)
[F(t) Bu]=first left block column of C(N)
Notes: This figure illustrates the basic steps in subspace identification of a state space model of a linear time invariant
(LTI) system.

## Slide 9: Two-Stage Modeling
We separate two kinds of factors and study their impacts on room temperatures independently
  (1) All power sources are deactivated. Only use ambient temperature Tamb(t) to predict the room temperatures Tnp(t): Tnp(t) = M1(Tamb(t))
  (2) Activate HVAC and other input effects and build model using input power P(t) to predict the temperature difference of each room with/without those extra inputs: Tall(t) - Tnp(t) = M2(P(t))

## Slide 10: Two-Stage Modeling Results
M1 model has low accuracy, implying ambient T has nonlinear impact on room temperatures
M2 model has higher accuracy. HVAC and other power inputs have more linear effects on Tall(t) - Tnp(t)

## Slide 11: Model order selection to avoid overfitting
Done various optimization which includes selecting a proper order.
For this order study, the best order seen below is 37. After many trials, we found an acceptable order.

## Slide 12: 5-zone Results (Training Phase)
For 5-zone building, only one zone and the first 500 hours shown below

## Slide 13: 5-zone Results (Validation Phase)

## Slide 14: Absolute and Relative Errors
Five zone with HVAC only considering ambient temperature |  |  |  |  |  | 
 |  | SPACE 1 | SPACE 2 | SPACE 3 | SPACE 4 | SPACE 5
Testing | Relative RMS Error | 0.0150 | 0.0165 | 0.0138 | 0.0136 | 0.0120
 | Max Relative Error | 0.0879 | 0.0825 | 0.0958 | 0.0927 | 0.0900
 | Absolute RMS Error | 0.3078 | 0.3372 | 0.2752 | 0.2739 | 0.2482
 | Max Absolute Error | 1.8780 | 1.7701 | 2.0544 | 1.9978 | 1.9546
Validation | Relative RMS Error | 0.0267 | 0.0290 | 0.0187 | 0.0199 | 0.0166
 | Max Relative Error | 0.1510 | 0.1868 | 0.1438 | 0.1463 | 0.1375
 | Absolute RMS Error | 0.5707 | 0.6267 | 0.3874 | 0.4157 | 0.3538
 | Max Absolute Error | 2.7525 | 4.1471 | 3.2361 | 3.3607 | 3.1209
Five zone with HVAC and considering extra factors |  |  |  |  |  | 
 |  | SPACE 1 | SPACE 2 | SPACE 3 | SPACE 4 | SPACE 5
Testing | Relative RMS Error | 0.0153 | 0.0167 | 0.0132 | 0.0139 | 0.0088
 | Max Relative Error | 0.0792 | 0.0948 | 0.0759 | 0.0788 | 0.0598
 | Absolute RMS Error | 0.3297 | 0.3620 | 0.2742 | 0.2919 | 0.1900
 | Max Absolute Error | 1.7938 | 2.0272 | 1.6310 | 1.6794 | 1.3117
Validation | Relative RMS Error | 0.0320 | 0.0333 | 0.0187 | 0.0203 | 0.0145
 | Max Relative Error | 0.1594 | 0.1690 | 0.0786 | 0.0930 | 0.0650
 | Absolute RMS Error | 0.7247 | 0.7520 | 0.3947 | 0.4352 | 0.3187
 | Max Absolute Error | 4.3228 | 4.6669 | 1.6876 | 2.0009 | 1.4297

## Slide 15: 2-Zone Results
For 2-zone, only one zone and first 500 hours are shown below
Two zone with HVAC and extra factors |  |  | 
 |  | SPACE 1 | SPACE 2
Testing | Relative RMS Error | 0.0021 | 0.0022
 | Max Relative Error | 0.0128 | 0.0144
 | Absolute RMS Error | 0.0476 | 0.0488
 | Max Absolute Error | 0.2959 | 0.3235
Validation | Relative RMS Error | 0.0041 | 0.0060
 | Max Relative Error | 0.0214 | 0.0229
 | Absolute RMS Error | 0.0939 | 0.1338
 | Max Absolute Error | 0.4912 | 0.5164

## Slide 16: Summary
Based on recently proposed subspace identification method
5-zone (all factors)
  1.4 - 3.3% average relative error
  6.5 – 16.9% max relative error
5-zone (HVAC only)
  1.7 – 2.9% average relative error
  13.8 – 18.7% max relative error
2-zone (all factors)
  0.4 – 0.6% average relative error
  2.1 – 2.3% max relative error

## Slide 17
Questions???